{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["多联机空调机组一二级保养","分体式空调一二级维保"],"not_rendered":{"images":2,"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"多联机空调机组一二级保养","index":0,"n_rows":24,"n_cols":12,"rows_kept":24,"merged":[[0,0,0,11],[1,0,1,2],[1,3,1,4],[1,5,1,6],[2,0,2,2],[2,3,2,4],[2,5,2,6],[3,1,3,2],[4,1,6,1],[7,1,17,1],[20,0,20,11],[21,0,22,5],[21,6,21,7],[21,8,21,9],[21,10,21,11],[22,6,22,7],[22,8,22,9],[22,10,22,11],[23,0,24,2],[23,3,23,4],[23,5,23,6],[23,7,23,8],[23,9,23,10],[24,3,24,4],[24,5,24,6],[24,7,24,8],[24,9,24,10]],"flags":["formulas_cached_only"]}
["设备维护保养单（一二级）-多联机空调机组"]
["物料代码",null,null,"物料描述",null,"出厂编号",null,"设备工装编号","上次维保时间","维保实施地点","开始维护日期","完成维护日期"]
[]
["序号","保养内容",null,"方法","合格要求","保养级别","保养周期（月）","计量器具编号","维保结果记录","更换添加的备件耗材代码","更换添加的备件耗材数量","备注"]
[1,"室内机","检查室内机外观","目视","外观完好，无破损和变形现象","二级",6]
[2,null,"检查控制开关各功能","目视、操作","室内机启停正常，温度变化明显，风速可以进行调整","二级",6]
[3,null,"检查空气过滤网堵塞情况","目视","无明显脏堵，翅片表面有金属光泽","二级",6]
[4,"室外机","检查室外机外观","目视","外观完好，无破损和锈蚀现象","二级",6]
[5,null,"检测压缩机工作电压、工作电流","测量","在有效范围内","二级",6]
[6,null,"检查压缩机油位、油质状态","目视，操作","油位达2/3，油质无明显浑浊","二级",6]
[7,null,"检测压缩机绕组的绝缘电阻","测量","在有效范围内","二级",6]
[8,null,"检查压缩机过载保护装置","操作","过载试验动作灵敏","二级",6]
[9,null,"通过压力表检测系统运行压力","操作","压力在有效范围内，并根据需要补充制冷剂","二级",6]
[10,null,"清洗换热器翅片","操作","无灰尘","二级",6]
[11,null,"检查散热风扇外观","目视","无损坏、无卡死","二级",6]
[12,null,"检测散热风扇电机工作电压、工作电流","测量","在有效范围内","二级",6]
[13,null,"检查交流接触器、热继电器动作情况","操作","动作正常，灵敏","二级",6]
[14,null,"检查线路是否有老化现象，电线是否紧固","操作","线路无老化，接线牢固","二级",6]
[15,"连接制冷剂管和电源线检查","检查管线外表的绑带情况","目视","绑带缠绕整齐，无破损现象","二级",6]
[16,"多联机液晶温控器","检查温控器功能","操作","温控器显示、按键等功能正常，温控器能够根据环境温度及时反馈","二级",6]
["保养单位（保养人员）要求：制冷与空调设备运行操作作业证、制冷与空调设备安装修理作业证、低压电工证、登高证"]
["注：\n①多人参与保养时，需在签名时列出各自保养内容的序号；\n②二级保养时需包含一级保养所有项目；\n③如由风电外部单位保养的，外部单位使用的计量器具需提供校准报告扫描件。\n④结果记录:有数值的记录数值，无数值的记录√或X，X的需说明后续处理项。",{"$nulls":5},"保养人/日期：",null,"使用人/日期:",null,"设备工装管理员/日期:"]
[]
["税后维保费用及质保期",null,null,"供应商维护费用（元）",null,"物流费用（元）",null,"配件抵扣金额（元）",null,"内部维护备件耗材费用（元）",null,"质保期（月）"]

{"sheet":"分体式空调一二级维保","index":1,"n_rows":14,"n_cols":12,"rows_kept":14,"merged":[[0,0,0,11],[1,0,1,2],[1,3,1,4],[1,5,1,6],[2,0,2,2],[2,3,2,4],[2,5,2,6],[3,1,3,2],[4,1,5,1],[6,1,9,1],[10,0,10,11],[11,0,12,5],[11,6,11,7],[11,8,11,9],[11,10,11,11],[12,6,12,7],[12,8,12,9],[12,10,12,11],[13,0,14,2],[13,3,13,4],[13,5,13,6],[13,7,13,8],[13,9,13,10],[14,3,14,4],[14,5,14,6],[14,7,14,8],[14,9,14,10]],"flags":["formulas_cached_only"]}
["设备维护保养单（一二级）-分体式空调"]
["物料代码",null,null,"物料描述",null,"出厂编号",null,"设备工装编号","上次维保时间","维保实施地点","开始维护日期","完成维护日期"]
[]
["序号","保养内容",null,"方法","合格要求","保养级别","保养周期（月）","计量器具编号","维保结果记录","更换添加的备件耗材代码","更换添加的备件耗材数量","备注"]
[1,"室内机","检查控制屏","操作","功能、显示正常","二级",6]
[2,null,"清洗室内机过滤网","操作","滤网洁净，无破损及变形","二级",6]
[3,"室外机","清洗外机翅片，","操作","翅片洁净，无倒片，无损坏及变形","二级",6]
[4,null,"管道保温层修补","操作","平整完好","二级",6]
[5,null,"检查紧固支架","操作，目视","无松动、无锈蚀","二级",6]
[6,null,"抽真空、加氟","操作","制冷剂无缺少","二级",6]
["保养单位（保养人员）要求：制冷与空调设备运行操作作业证、制冷与空调设备安装修理作业证、低压电工证、登高证"]
["注：\n①多人参与保养时，需在签名时列出各自保养内容的序号；\n②二级保养时需包含一级保养所有项目；\n③如由风电外部单位保养的，外部单位使用的计量器具需提供校准报告扫描件。\n④结果记录:有数值的记录数值，无数值的记录√或X，X的需说明后续处理项。",{"$nulls":5},"保养人/日期：",null,"使用人/日期:",null,"设备工装管理员/日期:"]
[]
["税后维保费用及质保期",null,null,"供应商维护费用（元）",null,"物流费用（元）",null,"配件抵扣金额（元）",null,"内部维护备件耗材费用（元）",null,"质保期（月）"]