## BOQ工程量清单
广以北校区科研楼R713、R426气路修缮项目参考工程量清单
BOQ of R713, R426 lab Replacement of gas line pressure reducing valve installation project
No. | Items | Project Characteristics Description | Qty. | Unit | Unit Price | Cost | 备注
序号 | 项目 | 项目特征描述 | 数量 | 单位 | 单价 | 总价 | Remarks
1 | （R426 实验室）二级减压阀 (R426 lab) The second pressure reducing valve | 1. 名称：二级减压阀 单表 2. 规格：1/4'' 3. 材质：SS-316L不锈钢BA级 4. 量程：0-0.16Mpa 1. Name: the second pressure reducing valve, single-meter model 2. 1/4'' 3. Material: SS-316L stainless steel BA grade 4. Range: 0-0.16Mpa | 6 | 个 Unit |  | 0 | 参考品牌：GCE、Swagelok、ULETEC或不低于此等级 Reference brand: GCE, Swagelok, ULETEC 阀门耐压>13Kg.f/cm2，大于学校一级减压阀的出口压力，防止误操作时阀门损坏。 The valve's pressure resistance is >13Kg.f/cm2, which is greater than the outlet pressure of the school's first-level pressure reducing valve to prevent valve damage during misoperation.
2 | （R713 实验室）二级减压阀(氢气) (R713 lab) The second pressure reducing valve（Hydrogen） | 1. 名称：二级减压阀 单表 2. 规格：1/4'' 3. 材质：SS-316L不锈钢BA级 4. 量程：0-16Mpa，使用压力40-80bar 1. Name: the second pressure reducing valve, single-meter model 2. 1/4'' 3. Material: SS-316L stainless steel BA grade 4. Range: 0-16Mpa,working pressure 40-80bar | 1 | 个 Unit |  | 0 | 参考品牌：GCE、Swagelok、ULETEC或不低于此等级 Reference brand: GCE, Swagelok, ULETEC 阀门耐压>160Kg.f/cm2，大于一级减压阀的出口压力，防止误操作时阀门损坏。 The valve's pressure resistance is >13Kg.f/cm2, which is greater than the outlet pressure of the school's first-level pressure reducing valve to prevent valve damage during misoperation.
3 | （R713 实验室）一级减压阀 (R713 lab) The first stage pressure reducing valve | 1. 名称：一级减压阀 双表 2. 规格：1/4'' 3. 材质：SS-316L不锈钢BA级 4. 量程：0-16Mpa，使用压力30-80bar 1. Name: the first stage pressure reducing valve, a double gauge model 2. 1/4'' 3. Material: SS-316L stainless steel BA grade 4. Range: 0-16Mpa,working pressure 30-80bar | 4 | 个 Unit |  | 0 | 参考品牌：GCE、Swagelok、ULETEC或不低于此等级 Reference brand: GCE, Swagelok, ULETEC
4 | 外丝卡套接头 Ferrule joint | 1. 名称：卡套接头 2. 规格：1/4'' 3. 材质：SS-316L不锈钢 1. Name: Ferrule joint 2. 1/4'' 3. Material: SS-316L stainless steel | 22 | 个 Unit |  | 0
5 | 新减压阀安装费 installation fee for the new pressure reducing valves |  | 11 | 个 Unit |  | 0
6 | 旧减压阀拆除费 Removal fee for the old pressure reducing valves |  | 11 | 个 Unit |  | 0
7 | 减压阀检测 Pressure reducing valves test |  | 5 | 个 Unit |  | 0 | R713实验室的5个阀门需送检到当地权威第三方检测，并出具检测报告。 The five valves in the R713 lab need to be sent the valves to the local authority to conduct the calibration and issued a test report.
8 | 气体系统调试 Gas system debugging | 1.内容：阀门保压试验 1. Valve pressure maintaining test | 2 | 项 Set |  | 0
9 | 实验室设备保护 Protection for construction area | 1. 内容：实验室设备防护 2. 保护材料：塑料防尘膜 1. Lab equipment protection 2. Plastic dust film | 2 | 项 Set |  | 0
10 | 安装辅材 Other auxiliary materials |  | 2 | 项 Set |  | 0
11 | 卫生清洁 Clean for construction area |  | 2 | 项 Set |  | 0
12 | 暂列金 Provisional sum |  | 1 | 项 Set | 2238 | 2238
13 | 税金9% Tax |  | 1 | 项 Set |  | 0
14 | 合计 In total |  |  |  |  | 2238
注： 1. 拆除的旧减压阀需要交还甲方 The removed old pressure reducing valve needs to be returned to Party A 2. 此次需更换减压阀的气体线路为惰性气体和氢气 The gas line of the pressure reducing valves that need to be replaced this time are inert gas and hydrogen 3.本次工程的质保期为2年 The warranty period of this project is 2 years. 4.工期：30天