{"text_format":"3","workbook":"xls","n_sheets":7,"sheets":["部件价格表","空调年度维护考核表","空调设备维修单","空调设备清洗记录表","多联机空调机组","转轮除湿机机","全新风空调机组"],"not_rendered":{"images":6,"comments":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"部件价格表","index":0,"n_rows":26,"n_cols":3,"rows_kept":26,"merged":[[0,0,0,2],[18,0,18,2]],"flags":["formulas_cached_only"]}
["电镜实验室多联机空调/除湿机部件维修价格表"]
[null,"Multi-connected AC unit","Price 价格"]
[1,"Multi-connected unit compressor 压缩机"]
[2,"Variable frequency control circuit board 变频基板"]
[3,"Filter electromagnetic wave circuit board 滤波基板"]
[4,"Multi-connected unit main board 室外机控制主板"]
[5,"High pressure sensor 高压传感器"]
[6,"Low pressure sensor 低压传感器"]
[7,"Four-way valve 四通阀"]
[8,"Electromagnetic expansion valve 电子膨胀阀阀体"]
[9,"Outdoor unit fan motor 室外机风扇电机"]
[10,"Relay 继电器"]
[11,"R410 refrigerant R410冷媒 10kg/瓶"]
[12,"Condenser 冷凝器"]
[13,"Evaporator 蒸发器"]
[14,"Controller 控制器"]
[]
[]
["Dehumidifier"]
[1,"Control system 控制系统"]
[2,"Fan 电风机"]
[3,"Heating module 加热模"]
[4,"High-temperature fan 高温风机"]
[5,"Travel switch 行程开关"]
[6,"Drainage Control Module 排水控制模块"]
[7,"Compressor 压缩机"]

{"sheet":"空调年度维护考核表","index":1,"n_rows":22,"n_cols":6,"rows_kept":22,"merged":[[0,0,0,5],[1,0,2,1],[1,2,2,2],[1,4,2,4],[1,5,2,5],[3,2,3,3],[4,0,5,0],[4,1,5,1],[4,2,5,3],[4,5,5,5],[6,0,7,0],[6,2,7,3],[6,4,7,4],[6,5,7,5],[8,0,9,0],[8,1,9,1],[8,2,8,3],[9,2,9,3],[10,0,11,0],[10,2,11,3],[10,4,11,4],[10,5,11,5],[12,0,13,0],[12,1,13,1],[12,2,12,3],[13,2,13,3],[14,2,14,3],[15,0,16,0],[15,2,16,3],[15,4,16,4],[15,5,16,5],[17,0,18,0],[17,2,18,3],[17,4,18,4],[17,5,18,5],[19,0,19,3],[20,0,20,1],[20,2,23,4],[20,5,23,5],[21,0,23,1]],"flags":["formulas_cached_only"]}
["广东以色列理工学院电镜室空调年度维护考核表"]
["维保单位",null,null,"考核","年度 ","备注"]
[{"$nulls":3},"周期"]
["序号","考核项目","考核内容",null,"得分"]
[1,"强制条款","履约中是否存在下列情形：1.  质量伪劣；2. 不守信誉；3.被公开曝光；4.出现安全事故；5.对存在问题未按要求整改或被处以停业、吊销相关资质证等。若存在可直接评价为不合格。",null,"合格"]
[{"$nulls":4},"口不合格"]
[2,"服务质量","维保服务符合现行相关国家规范、标准和行业要求:所需设备，备件，材料等符合现行相关国家规范，技术要求及质量标准；满足三菱多联机、鑫松除湿机和天加新风机维保服务的技术指标、质量要求。验收合格率达到100%，13～15分；维护首验不合格通过整改后验收合格，6～12分；二次以上验收不合格，0～6分。每项不合格扣1分。"]
[null,"（15分)"]
[3,"应急服务处理(20分）","技术支持：主动有效，8～10分；被动有效，4～8分；被动无效，0分。每项不合格扣2分。"]
[null,null,"应急服务:：及时，9～10分；被动，2～8分；消极，0～3分。每项不合格扣1分"]
[4,"安全防范","遵守学校规章制度，安全责任心强。安全措施到位，9～10分；安全措施欠缺积极整改的，3～8分；安全措施不到位且未按要求整改的，0～3分。每项不合格扣1分。"]
[null,"(10分)"]
[5,"服务及时性（20分）","按时完成日常维保及紧急故障处理，10分；有3次以及下未按期完成的，5分；有3次以上未按期完成的，0分。"]
[null,null,"服务响应时间符合承诺，紧急故障事项30分钟内到达现场，10 分；履约中出现未按服务响应时间承诺到达现场的，每次不响应扣2分。"]
[6,"设备保养有效性（15分）","能及时按合同需求计划时间进行保养，保养效果良好，12～15分；缺少保养和检查，或设备保养质量一般，3～12分；没按计划进行保养，导致设备运行状态差，0分。每项不合格扣1分。"]
[7,"有效性","相关项目团队人员配备齐全，分工合理，在技支术持、备品备件等方面能够满足学校方电镜室空调维保的需要，有效协调工作开展，8～10分；存在不足的，0～8分。每项不合格扣2分。"]
[null,"（10分）"]
[8,"服务态度","相关方服务人员礼貌和蔼、服务周到，“用户第一”思想贯穿技术支持、维护保养、更换设备、清洗等项目全过程，8～10分；存在不足的，0～8分。每项不合格扣2分。"]
[null,"(10分)"]
["考核总分"]
["考评务服结论"]
["考核总分85分（含85分）以上为“优”按合同支付服务费；低于85分为“良好”每扣1分按年维保费的1%扣除；低于65分为“差”视为考核不合格，按年维保费的30%扣除；全年两次考核不合格启动退出机制。"]

{"sheet":"空调设备维修单","index":2,"n_rows":20,"n_cols":8,"rows_kept":20,"merged":[[0,0,1,1],[0,2,1,4],[0,5,0,6],[1,5,1,6],[2,0,2,4],[2,5,2,7],[3,0,5,0],[3,1,3,7],[4,1,4,7],[5,1,5,3],[5,4,5,5],[5,6,5,7],[6,1,6,3],[6,4,6,7],[7,0,8,0],[7,1,7,2],[7,3,7,4],[7,5,7,6],[8,1,8,2],[8,3,8,4],[8,5,8,6],[9,0,10,0],[9,1,9,2],[9,5,9,7],[10,1,10,2],[10,5,10,7],[11,0,12,0],[11,1,12,7],[13,0,16,0],[13,1,14,2],[13,5,13,6],[14,3,14,7],[15,1,15,7],[16,1,16,7],[17,0,18,0],[17,1,17,2],[17,5,17,6],[18,1,18,2],[18,5,18,6],[19,0,19,7]],"flags":["formulas_cached_only"]}
[null,null,"广东以色列理工学院",null,null,"编号",null,"GTIIT/2025-2026"]
[{"$nulls":5},"页码",null,"第1页 / 共1页"]
["电镜空调设备维修单（GTIIT HVAC)",{"$nulls":4},"文件类型：附件"]
["故障\n情况","所属校区：□北校区    \n故障描述："]
[null,"按故障发生时间分类：□早发性故障 □突发性故障 □渐进性故障 □复合型故障\n按故障类型分类：□程序故障 □电气故障 □机械故障 □液压故障□其他故障\n紧急程度：□紧急 □非紧急\n引起的额外损失：□财产损失 □人员受伤\n"]
[null,"实物位置：",null,null,"报修人： ",null,"报修日期："]
["对应\n措施","是否在质保期内：□ 是      □否",null,null,"故障责任： □供方原因   □内部原因   □自然原因"]
["维修记录（维修人员\n填写）","故障分析",null,"维修服务内容",null,"更换的部件或零件（型号、规格、品牌、数量等）",null,"维修人员及日期"]
[]
["维修工时","维修开始时间",null,"维修结束时间","维修工时","设备管理员"]
[]
["备注","□ 维修服务内容与《广东以色列理工学院空调设备维保方案》一致；\n□维修服务内容与《广东以色列理工学院空调设备维保方案》不一致，另外附页说明与维修方案差异的部分"]
[]
["维修验收","维修结论",null,"□故障全部消除","□故障部分消除，可使用","□故障未消除，无法使用",null,"□其他"]
[{"$nulls":3},"后续需跟踪项："]
[null,"维修单位名称"]
[null,"武汉康尔斯特电磁屏蔽科技有限公司   "]
["税后维修费用及质保期\n（更换配件超500元）","供应商维修费用\n（元）",null,"物流费用（元）","配件抵扣金额\n（元）","维修配件耗材费用（元）",null,"质保期（月）"]
[]
["其他说明项：\n"]

{"sheet":"空调设备清洗记录表","index":3,"n_rows":13,"n_cols":8,"rows_kept":13,"merged":[[0,0,1,1],[0,2,1,4],[0,5,0,6],[1,5,1,6],[2,0,2,4],[2,5,2,7],[3,0,5,0],[3,1,3,7],[4,1,4,7],[5,1,5,3],[5,4,5,5],[5,6,5,7],[6,1,6,3],[6,4,6,7],[7,0,8,0],[7,1,7,2],[7,5,7,7],[8,1,8,2],[8,5,8,7],[9,0,12,0],[9,1,10,2],[9,5,9,6],[10,3,10,7],[11,1,11,2],[11,3,11,7],[12,1,12,2],[12,3,12,7]],"flags":["formulas_cached_only"]}
[null,null,"广东以色列理工学院",null,null,"编号",null,"GTIIT/2025-2026"]
[{"$nulls":5},"页码",null,"第1页 / 共1页"]
["电镜室空调设备清洗记录表（GTIIT HVAC)",{"$nulls":4},"文件类型：附件"]
["基本信息","①清洗方案：\n室内机：拆下面盖，均匀喷清洁剂于蒸发器，清洗室内/外机过滤网、盘管、管道等，用  高压水枪冲洗洗蒸发器上散热翅片，装回拆下部件；\n冷水系统空调末端机组深度清洗蒸发器、托水盘，过滤网，面板外观保洁及清通管道；\n室外机：用高压水枪均匀喷洒清洁室外机散热翅片/冷却塔填料并擦拭外观，同时清除异物；\n恒温恒湿机和全新风系统：恒压自来水冲洗风口滤网，清洁表冷器和风机盘管及其积水盘，并擦拭机组外观；\n②清洗效果：\n确保蒸发器和进风口、出风口清洁，保持风机表面及风管外面清洁；\n确保室外机散热良好，外观清洁；\n确保室外机组散热翅片清洁；\n确保全新风机机组和恒温恒湿机组进风口滤网清洁，风机盘管、表冷器和水盘清洁无杂物；\n确保冷却塔外观干净，填料清洁无杂物，托水盘清洁，水质良好；"]
[null,"清洗区域："]
[null,"空调设备位置：",null,null,"清洁人员： ",null,"日期："]
["对应措施（管理员填写）","是否在质保期内：□ 是      □否",null,null,"清洗频率："]
["清洁工时","开始时间",null,"结束时间","清洁工时","设备管理员"]
[]
["清洗保养验收","清洁效果\n（抑菌/消毒/散热）",null,"□良好","□一般","□较差",null,"□其他"]
[{"$nulls":3},"后续需跟踪项："]
[null,"维保单位名称"]
[null,"验收人员"]

{"sheet":"多联机空调机组","index":4,"n_rows":26,"n_cols":11,"rows_kept":26,"merged":[[0,0,0,10],[1,0,1,10],[2,1,2,2],[3,1,7,1],[8,1,20,1],[23,0,23,10],[24,0,24,10],[25,0,26,4],[25,5,25,6],[25,7,25,8],[25,9,25,10],[26,5,26,6],[26,7,26,8],[26,9,26,10]],"flags":["formulas_cached_only"]}
["设备维护保养单-多联机空调机组"]
["维保区域："]
["序号","保养内容",null,"方法","合格要求","保养周期（月）","计量器具编号","维保结果数值记录","更换添加的备件耗材代码","更换添加的备件耗材数量","备注"]
[1,"室内机","检查室内机外观","目视","外观完好，无破损和变形现象",6]
[2,null,"检查控制开关各功能","目视、操作","室内机启停正常，温度变化明显，风速可以进行调整",6]
[3,null,"检查室进出风口、温度","测量","出风温度和回风温度正常",6]
[4,null,"检查室内机是否异响、滴水等","目视、操作","室内机无异响、漏水",6]
[5,null,"检查空气过滤网堵塞情况","目视","无明显脏堵，翅片表面有金属光泽",6]
[6,"室外机","检查室外机外观","目视","外观完好，无破损和锈蚀现象",6]
[7,null,"检查管路和压缩机","目视","是否异常或结霜",6]
[8,null,"检测压缩机工作电压、工作电流、三相平衡度","测量","在有效范围内",6]
[9,null,"检查压缩机油位、油质状态","目视，操作","油位达2/3，油质无明显浑浊",6]
[10,null,"检测压缩机绕组的绝缘电阻","测量","在有效范围内",6]
[11,null,"检查压缩机过载保护装置","操作","过载试验动作灵敏",6]
[12,null,"通过压力表检测系统运行压力","操作","压力在有效范围内，并根据需要补充制冷剂",6]
[13,null,"清洗换热器翅片","操作","无灰尘",6]
[14,null,"检查室外机噪声、振动、异味","目视","无噪声、振动、异味",6]
[15,null,"检查散热风扇外观","目视","无损坏、无卡死",6]
[16,null,"检测散热风扇电机工作电压、工作电流、噪声等","测量","在有效范围内，电机轴承润滑",6]
[17,null,"校正高低压开关","操作","动作正常，灵敏",6]
[18,null,"检查线路是否有老化现象，电线是否紧固","操作","线路无老化，接线牢固",6]
[19,"连接制冷剂管和电源线检查","检查管线外表的绑带情况、保温层","目视","绑带缠绕整齐，无破损现象，保温层无开裂、破损、漏水",6]
[20,"多联机集控系统","检查多联机集中控制系统","操作","系统操作正常，温控器能够根据环境温度及时反馈",6]
["维保情况说明："]
["保养单位："]
["注：\n①多人参与保养时，需在签名时列出各自保养内容的序号；\n②如由风电外部单位保养的，外部单位使用的计量器具需提供校准报告扫描件；\n③结果记录:有数值的记录数值，无数值的记录√或X，X的需说明后续处理项；\n",{"$nulls":4},"保养人/日期：",null,"使用人/日期:",null,"设备管理员/日期"]

{"sheet":"转轮除湿机机","index":5,"n_rows":27,"n_cols":11,"rows_kept":27,"merged":[[0,0,0,10],[1,0,1,10],[2,1,2,2],[3,1,5,1],[6,1,10,1],[12,1,14,1],[15,1,20,1],[21,1,23,1],[24,0,24,10],[25,0,25,10],[26,0,27,4],[26,5,26,6],[26,7,26,8],[26,9,26,10],[27,5,27,6],[27,7,27,8],[27,9,27,10]],"flags":["formulas_cached_only"]}
["设备维护保养单-转轮除湿机"]
["维保区域："]
["序号","保养内容",null,"方法","合格要求","保养周期（月）","计量器具编号","维保结果记录","更换添加的备件耗材代码","更换添加的备件耗材数量","备注"]
[1,"转轮除湿系统","检查转轮除湿是否正常运转","测量","转轮除湿转盘转动正常，除湿芯无堵塞，电机链条传动平稳",6]
[2,null,"转轮电机固定螺栓紧固/接线盒接线端子","操作","螺丝无松动现象",6]
[3,null,"检测转轮电机绕组的绝缘电阻","测量","在有效范围内",6]
[4,"风机系统","检查离心风机及电机的运行状况，测量电机工作电压、工作电流等参数","测量","在有效范围内",6]
[5,null,"风机轴承加注润滑油","操作","新油挤出",6]
[6,null,"校正传动皮带的张紧度，更换已磨损的传动部件","操作","张紧度合适，部件无存在磨损",6]
[7,null,"检查导风叶轮","操作","检查导风叶轮有无污物和磨损",6]
[8,null,"检查风机电机紧固情况，及时拧紧固定件","操作","螺丝无松动现象",6]
[9,"过滤段","清洗出风和回风滤网","操作","无灰尘",6]
[10,"再生热系统","检查不锈钢电加热管","操作","无破裂，绝缘电阻在0.5MΩ以内",6]
[11,null,"检查温度传感器","测量","测量温度传感器电阻和房间实测反馈温度是否正常",6]
[12,null,"校正辅热和再生热装置的控制参数","操作","符合安全性能的要求",6]
[13,"电气系统","检查空气开关、交流接触器、热继电器、微继电器动作情况，确保各其运行正常","操作","动作正常",6]
[14,null,"检查各传感装置感测灵敏度是否正常，及时修复或更换","操作","灵敏度符合要求",6]
[15,null,"检查电控箱整洁","操作","电控箱无灰尘杂物",6]
[16,null,"检查液晶集中控制器","检查","检查液晶集中控制显示正常，无报警",6]
[17,null,"检查控制器、手操器，校正机组控制参数","操作","控制参数符合实际使用要求",6]
[18,null,"接线端子有无松动","操作","压实无松动",6]
[19,"整机调试","电控系统模拟调试，检查各电器动作、程序是否合符要求","操作","运行状态正常",6]
[20,null,"整体和管道固定情况","检查","整体基座与地面固牢固，管道无振动异响",6]
[21,null,"开机精准调试","操作","工况正常",6]
["维保情况说明："]
["保养单位："]
["注：\n①多人参与保养时，需在签名时列出各自保养内容的序号；\n②如由风电外部单位保养的，外部单位使用的计量器具需提供校准报告扫描件；\n③结果记录:有数值的记录数值，无数值的记录√或X，X的需说明后续处理项；\n",{"$nulls":4},"保养人/日期：",null,"使用人/日期:",null,"设备管理员/日期"]

{"sheet":"全新风空调机组","index":6,"n_rows":28,"n_cols":11,"rows_kept":28,"merged":[[0,0,0,10],[1,0,1,10],[2,1,2,2],[3,1,7,1],[9,1,13,1],[14,1,18,1],[19,1,21,1],[22,1,24,1],[25,0,25,10],[26,0,26,10],[27,0,28,4],[27,5,27,6],[27,7,27,8],[27,9,27,10],[28,5,28,6],[28,7,28,8],[28,9,28,10]],"flags":["formulas_cached_only"]}
["设备维护保养单-全热交换新风机组"]
["维保区域："]
["序号","保养内容",null,"方法","合格要求","保养周期（月）","计量器具编号","维保结果记录","更换添加的备件耗材代码","更换添加的备件耗材数量","备注"]
[1,"风机系统","检查离心风机及电机的运行状况，测量电机工作电压、工作电流等参数","测量","在有效范围内",6]
[2,null,"风机轴承加注润滑油","操作","新油挤出",6]
[3,null,"检查导风叶轮","操作","检查导风叶轮有无污物和磨损",6]
[4,null,"风量和风压检测","测量","风量和风压正常",6]
[5,null,"检查风机电机紧固情况，及时拧紧固定件","操作","螺丝无松动现象",6]
[6,"过滤段","全热过滤网更换或清洗、消毒","操作","清洗后用手触摸后,没有尘土",6]
[7,"系统参数","检查管道\n和风阀","操作","开启关闭正常，无卡死，有锈蚀及时刷漆和润滑修复",6]
[8,null,"检查新风出风温度","检查测量","新风出风温度与设置一直",6]
[9,null,"检查新排风阀门联动","检查","检查新排风联动风量是否正常",6]
[10,null,"检查温度传感器","测量","测量各温度传感器电阻和房间实测反馈温度是否正常",6]
[11,null,"检查风管和风阀灵敏度","操作","风管无漏风，风阀无卡阻",6]
[12,"电控系统","校对压力保护开关和控制阀体的设定值","操作","设定值符合要求",6]
[13,null,"检查各传感装置感测灵敏度是否正常，及时修复或更换","操作","灵敏度符合要求",6]
[14,null,"检查电控箱整洁","操作","电控箱无灰尘杂物",6]
[15,null,"检查控制器、手操器，校正机组控制参数","操作","控制参数符合实际使用要求",6]
[16,null,"接线端子有无松动","操作","压实无松动",6]
[17,"机体结构清洁及维护","检查机体内、外各零部件的紧固情况","操作","各零件结构牢固，无松动",6]
[18,null,"检查箱体密封情况","触摸","无漏风",6]
[19,null,"整体设备外观清洁","操作","外观整洁，无灰尘",6]
[20,"整机调试","电控系统模拟调试，检查各电器动作、程序是否合符要求","操作","运行状态正常",6]
[21,null,"整体固定情况","检查","整体基座与地面固牢固",6]
[22,null,"开机精准调试","操作","工况正常",6]
["维保情况说明："]
["保养单位："]
["注：\n①多人参与保养时，需在签名时列出各自保养内容的序号；\n②如由风电外部单位保养的，外部单位使用的计量器具需提供校准报告扫描件；\n③结果记录:有数值的记录数值，无数值的记录√或X，X的需说明后续处理项；\n",{"$nulls":4},"保养人/日期：",null,"使用人/日期:",null,"设备管理员/日期"]